October 16, 2020

John F. Cavoli, P.E.

Cavoli Engineering, Inc.

5824 Bee Ridge Road, #325

Sarasota, Florida 34240

Subject:	Community Day School Campus

Application No. 20-147895-UP

Dear Mr. Cavoli:

We have reviewed your construction plans submitted for the subject project. Attached please find our review comments.

The outcome of our review is identified below:

[   ]	Plans approved.

[   ]	Plans approved with stipulations, and/or comments to be addressed at Utility Construction Permit phase.

[X]	Plans disapproved.  Please resubmit two sets of revised plans.

All future submittals should reference the application number identified in the subject line above.

If your plans are approved or approved with stipulations, you may now apply for the Utility Construction Permit and/or FDEP Permits.

If you have any questions, please contact this office at 941/861-6625 or the reviewer identified at the end of the comments attached.

Submittals and applicable review fees must be delivered to Veronica Ford, Public Utilities, 1001 Sarasota Center Boulevard, Sarasota, Florida 34240. All responses shall be described in a cover letter and clearly identified on the plans.

Sincerely,

Michael M. Mehan, P.E.

Utilities Regulatory Supervisor

MMM:vaf

Cc: Ramon Diaz, Senior Utility Inspector

- All Utility permitting submittals shall be submitted to Veronica Ford, Utilities Permitting Coordinator II, at 1001 Sarasota Center Blvd., Sarasota, FL 34240.

- The Engineer of Record shall notify UTILITIES in writing if revised plans cannot be returned within thirty (30) days. A request for an extension of up to ninety (90) days can be made. If there is no response to a returned set of documents within ninety (90) days UTILITIES will consider the plan review automatically canceled by the applicant. Re-submittal of the plans after this period will be subject to applicable review fees.

- General – A full set of the Utility Construction plans shall be submitted in .pdf (all pages bound) form on CD for all utility plan submittals. Please bind the files into 1 pdf file (do not send in individual pages)

- General – All proposed on-site easements must be reviewed and approved by Sarasota County Utilities and recorded by Public Works/Real Property of Sarasota County prior to issuance of any Cos, TCOs or business license if applicable. All Public Utility Easements shall be reviewed by Utilities prior to being sent to Real Property.

- General – Please add the following note on the plans: Sarasota County Public Utilities acknowledges the existing duplex grinder pump station may serve the existing and proposed site improvements with conditions.  The shower facilities in the gymnasium may not be used for any organized sporting team.  There shall be no onsite cafeteria for the school. If any one of these conditions are violated, then a Sarasota County standard lift station shall be required to serve the parcel prior to any future development of the site is approved.

- Sheet 9 – Please provide a profile for the fire line in accordance with UWWRWSC Sec. 6.3.7.a-.f. Please include both storm pipe crossings in the profile. 2nd request, please provide a separate profile for the fire line. The profile currently provided is not accurately portrayed and 1-storm pipe crossing is missing.

- Sheet 9 – For the connection to the existing manhole, in accordance with UWWRWSC Sec. 13.9.2. please add the following note: Additional pipe connections or modification of the existing factory made openings required on new or existing precast concrete manholes shall be performed only by means of core drilling, in accordance with manufacturer's recommendations for installing a neoprene boot, link seal or equal. Flexible connectors shall conform to ASTM C923, latest revision.

- Please verify that the existing 2” backflow preventer for the 2” domestic water service is a reduced pressure type BFP and verify that it has current testing and certification. If it is not an RPZ type an RPZ type will need to be provided.

- Please remove the proposed connection from the existing well located in the gym to the proposed potable watermain.

If you wish to discuss these review comments please contact Wayne Disbrow

at (941) 258-8173 or rdisbrow@scgov.net.